## Slide 1: Independent Load Forecast Workshop
September 26, 2016

## Slide 2: July Workshop
Updated load forecast comparison (Module E and ILF)
State forecast results
Updated allocation factors

## Slide 3: Data Update
MISO provided a new historical dataset that closely matches previous data
That dataset was used here and for the weather normalization

## Slide 4: Weather Normalization
Based on stakeholder comments and at the request of MISO, we used the ILF models to determine weather normal historical energy and peak demand values for 2011 to 2015
Process description and results are provided as a separate document

## Slide 5: Louisiana Model
In the July workshop, different options were presented for the Louisiana econometric model
Option 1 (which disregards 2005 from history) was chosen and was used for the work presented here

## Slide 6: Energy to Peak Models

## Slide 7: Stakeholder Comment 2015
In 2015 we used an after-the fact adjustment to correct for bias in the model result
  The models provided mean load for a given temperature, but peaks occur at the tails of the distribution
It was suggested that we use binary variables instead
  We have implemented this; some binary variables have weak statistical significance but the results of this model formulation were not directionally biased

## Slide 8: Selected Weather Stations
Hourly weather data source: Midwest Regional Climate Center
Weather STATION | Zone
Minneapolis St Paul International Airport MN | LRZ 1
Milwaukee Mitchell International Airport WI | LRZ 2
Des Moines International Airport IA | LRZ 3
Springfield Abraham Lincoln Capital Airport IL | LRZ 4
St Louis Lambert International Airport MO | LRZ 5
Indianapolis International Airport IN | LRZ 6
Lansing Capital City Airport MI | LRZ 7
Little Rock Airport Adams Field AR | LRZ 8
Lake Charles Regional Airport LA | LRZ 9
Jackson International Airport MS | LRZ 10

## Slide 9: Methodology
Hourly loads for each LRZ from 2010-2015 were used
Daily peak loads for winter/summer were used, except weekends and holidays
Separate winter/summer peak models
Ratio of annual average load to peak load was used to account for changing baselines over time
  Similar to load factor, but used for winter as well

## Slide 10: Explanatory Variables
Average daily temperature
Hourly temperature
Maximum daily temperature
Average of temperature for the last 3 hours

## Slide 11: Data Limitations
Six years’ worth of data is a small sample size for determining peaks
As we get more data, changes from one year to the next seem to be getting smaller (as expected)
  Changes in model formulation from year to year makes it impossible to say that the increase in data is the cause

## Slide 12: Normal Conditions on Peak
We estimated the normal weather conditions that occur during the summer and winter peak using the same process as last year
  Actual conditions during peak are only known for 6 years (2010-2015), which is too short to determine normal
  Actual weather conditions for 1997-2009 were also used to supplement the data

## Slide 13: Peak Weather Normalization
Hourly zonal temperature, 1997 to 2015
Actual hourly zonal loads, 2010 to 2015
actual peak hours
Normal zonal peak weather condition
actual peak weather conditions
rank hourly temperature records (excluding hours where peak demands do not occur)
potential peak hours

## Slide 14: Normal Temperatures (oF) on Peak
LRZ | Winter |  |  |  | Summer |  |  | 
 | Hourly Temp | Average Daily Temp | Daily Max Temp | Moving Average Temp | Hourly Temp | Average Daily Temp | Daily Max Temp | Moving Average Temp
LRZ 1 | 3.9 | 7.9 | 19.5 | 4.2 | 93.7 | 84.8 | 94.7 | 93.6
LRZ 2 | 2.8 | 3.9 | 11.2 | 3.2 | 91.3 | 81.4 | 92.1 | 91.6
LRZ 3 | 3.2 | 2.3 | 12.4 | 4.0 | 93.6 | 86.2 | 96.3 | 95.0
LRZ 4 | 3.0 | 9.5 | 18.8 | 3.5 | 93.6 | 84.9 | 94.6 | 93.8
LRZ 5 | 9.5 | 14.6 | 27.9 | 8.7 | 98.3 | 90.4 | 99.7 | 98.8
LRZ 6 | 4.0 | 11.6 | 21.1 | 3.8 | 91.2 | 83.0 | 92.1 | 91.2
LRZ 7 | 13.5 | 13.1 | 21.6 | 14.2 | 88.8 | 80.7 | 92.3 | 90.2
LRZ 8 | 19.9 | 26.3 | 36.6 | 18.9 | 100.9 | 88.9 | 101.9 | 100.7
LRZ 9 | 31.9 | 37.3 | 50.1 | 28.8 | 93.9 | 86.1 | 98.5 | 95.2
LRZ 10 | 27.2 | 31.0 | 43.2 | 22.9 | 93.7 | 86.3 | 98.6 | 95.6

## Slide 15: Ratio of Average Load to Peak Load under Normal Peak Weather Conditions
LRZ | 2016 study |  | 2015 study | 
 | Summer | Winter | Summer | Winter
LRZ 1 | 0.63803 | 0.76396 | 0.64888 | 0.75224
LRZ 2 | 0.60994 | 0.77340 | 0.58997 | 0.74869
LRZ 3 | 0.61000 | 0.75481 | 0.61145 | 0.75597
LRZ 4 | 0.59594 | 0.73795 | 0.58583 | 0.74201
LRZ 5 | 0.57363 | 0.68207 | 0.57422 | 0.68922
LRZ 6 | 0.65497 | 0.72549 | 0.66301 | 0.72876
LRZ 7 | 0.56128 | 0.78621 | 0.55809 | 0.77737
LRZ 8 | 0.56981 | 0.68425 | 0.57952 | 0.69069
LRZ 9 | 0.63384 | 0.71290 | 0.65123 | 0.72070
LRZ 10 | 0.54722 | 0.63749 | 0.54604 | 0.67146

## Slide 16: Comparison Charts
LRZ_LF_S: the zonal actual summer peak load factor
LRZ_LFF_S: the fitted zonal summer peak load factor given actual peak weather condition
Norm LF_S: the fitted normal summer peak load factor under normal weather condition
A similar process was done for winter peaks but is not shown here

## Slide 17
Seasonal Peaks—Actual vs. Fitted (LRZ1)
DT_1_S | TEMP_1_S | AVGT_1_S | MAXT_1_S | MAVGT3_1_S
8/9/2010 15:00 | 93.00 | 84.33 | 94.00 | 93.33
7/20/2011 16:00 | 95.00 | 89.21 | 96.00 | 95.33
7/2/2012 14:00 | 98.00 | 88.08 | 99.00 | 97.00
8/26/2013 14:00 | 96.00 | 87.38 | 96.00 | 94.33
7/21/2014 15:00 | 91.00 | 82.46 | 91.00 | 90.67
8/14/2015 15:00 | 91.00 | 82.17 | 93.00 | 92.00
Norm | 93.68 | 84.75 | 94.68 | 93.62

## Slide 18
Seasonal Peaks—Actual vs. Fitted (LRZ2)
DT_2_S | TEMP_2_S | AVGT_2_S | MAXT_2_S | MAVGT3_2_S
8/12/2010 15:00 | 87.00 | 80.50 | 88.00 | 87.67
7/20/2011 16:00 | 97.00 | 86.88 | 98.00 | 97.33
7/16/2012 15:00 | 96.00 | 86.96 | 97.00 | 96.00
8/27/2013 15:00 | 94.00 | 84.46 | 94.00 | 94.00
7/22/2014 16:00 | 87.00 | 79.04 | 89.00 | 87.33
8/14/2015 15:00 | 93.00 | 79.33 | 93.00 | 92.67
Norm | 91.25 | 81.42 | 92.13 | 91.65

## Slide 19
Seasonal Peaks—Actual vs. Fitted (LRZ3)
DT_3_S | TEMP_3_S | AVGT_3_S | MAXT_3_S | MAVGT3_3_S
8/12/2010 15:00 | 93.00 | 85.96 | 94.00 | 93.67
7/19/2011 17:00 | 95.00 | 88.50 | 98.00 | 96.67
7/25/2012 16:00 | 105.00 | 90.88 | 106.00 | 105.33
9/9/2013 16:00 | 97.00 | 86.13 | 101.00 | 99.00
9/4/2014 16:00 | 91.00 | 83.58 | 93.00 | 92.00
7/17/2015 16:00 | 94.00 | 85.46 | 95.00 | 94.67
Norm | 93.63 | 86.17 | 96.32 | 95.04

## Slide 20
Seasonal Peaks—Actual vs. Fitted (LRZ4)
DT_4_S | TEMP_4_S | AVGT_4_S | MAXT_4_S | MAVGT3_4_S
8/3/2010 16:00 | 94.00 | 85.38 | 95.00 | 94.67
7/21/2011 16:00 | 97.00 | 87.71 | 98.00 | 97.33
7/25/2012 16:00 | 101.00 | 90.71 | 103.00 | 102.00
8/30/2013 15:00 | 93.00 | 83.00 | 94.00 | 93.67
8/25/2014 15:00 | 96.00 | 85.21 | 96.00 | 95.00
7/13/2015 16:00 | 91.00 | 83.92 | 93.00 | 91.67
Norm | 93.58 | 84.93 | 94.62 | 93.84

## Slide 21
Seasonal Peaks—Actual vs. Fitted (LRZ5)
DT_5_S | TEMP_5_S | AVGT_5_S | MAXT_5_S | MAVGT3_5_S
8/3/2010 16:00 | 100.00 | 91.50 | 102.00 | 100.67
8/2/2011 16:00 | 101.00 | 91.92 | 102.00 | 101.67
7/25/2012 16:00 | 106.00 | 96.33 | 107.00 | 106.33
8/30/2013 15:00 | 99.00 | 89.92 | 100.00 | 99.67
8/25/2014 16:00 | 95.00 | 89.33 | 98.00 | 95.67
7/13/2015 16:00 | 97.00 | 89.67 | 98.00 | 97.67
Norm | 98.25 | 90.36 | 99.69 | 98.81

## Slide 22
Seasonal Peaks—Actual vs. Fitted (LRZ6)
DT_6_S | TEMP_6_S | AVGT_6_S | MAXT_6_S | MAVGT3_6_S
8/10/2010 16:00 | 96.00 | 87.13 | 96.00 | 95.67
7/20/2011 14:00 | 98.00 | 87.71 | 98.00 | 96.00
7/25/2012 16:00 | 99.00 | 87.79 | 102.00 | 101.00
7/18/2013 15:00 | 91.00 | 84.13 | 93.00 | 91.33
9/5/2014 15:00 | 88.00 | 79.08 | 89.00 | 88.33
7/29/2015 14:00 | 88.00 | 81.25 | 90.00 | 89.00
 | 91.16 | 83.04 | 92.11 | 91.21

## Slide 23
Seasonal Peaks—Actual vs. Fitted (LRZ7)
DT_7_S | TEMP_7_S | AVGT_7_S | MAXT_7_S | MAVGT3_7_S
7/7/2010 15:00 | 91.00 | 82.42 | 92.00 | 91.33
7/21/2011 14:00 | 95.00 | 85.46 | 96.00 | 94.33
7/17/2012 15:00 | 98.00 | 86.88 | 98.00 | 97.33
7/17/2013 14:00 | 92.00 | 83.63 | 93.00 | 91.33
9/5/2014 15:00 | 86.00 | 76.71 | 88.00 | 87.00
7/28/2015 15:00 | 77.00 | 78.83 | 91.00 | 85.33
Norm | 88.84 | 80.72 | 92.27 | 90.15

## Slide 24
Seasonal Peaks—Actual vs. Fitted (LRZ8)
DT_8_S | TEMP_8_S | AVGT_8_S | MAXT_8_S | MAVGT3_8_S
8/2/2010 15:00 | 103.00 | 89.25 | 104.00 | 103.33
8/3/2011 14:00 | 111.00 | 95.79 | 113.00 | 111.67
7/30/2012 14:00 | 111.00 | 94.63 | 111.00 | 108.67
7/9/2013 16:00 | 96.00 | 86.50 | 96.00 | 96.00
8/25/2014 13:00 | 96.00 | 85.42 | 96.00 | 95.33
7/29/2015 15:00 | 98.00 | 90.25 | 101.00 | 99.33
Norm | 100.92 | 88.91 | 101.89 | 100.69

## Slide 25
Seasonal Peaks—Actual vs. Fitted (LRZ9)
DT_9_S | TEMP_9_S | AVGT_9_S | MAXT_9_S | MAVGT3_9_S
8/2/2010 16:00 | 95.00 | 87.50 | 104.00 | 96.67
8/31/2011 16:00 | 94.00 | 85.13 | 99.00 | 95.00
6/26/2012 16:00 | 96.00 | 88.04 | 103.00 | 97.67
8/7/2013 16:00 | 91.00 | 86.13 | 97.00 | 92.67
8/22/2014 16:00 | 90.00 | 83.83 | 93.00 | 91.33
8/10/2015 15:00 | 99.00 | 88.42 | 100.00 | 99.33
Norm | 93.95 | 86.09 | 98.47 | 95.16

## Slide 26
Seasonal Peaks—Actual vs. Fitted (LRZ10)
DT_10_S | TEMP_10_S | AVGT_10_S | MAXT_10_S | MAVGT3_10_S
8/2/2010 14:00 | 104.00 | 88.75 | 104.00 | 103.67
8/3/2011 14:00 | 87.00 | 89.38 | 98.00 | 90.00
7/30/2012 16:00 | 90.00 | 88.54 | 98.00 | 93.33
8/8/2013 16:00 | 96.00 | 86.75 | 97.00 | 96.33
8/6/2014 16:00 | 94.00 | 83.29 | 95.00 | 94.67
8/10/2015 15:00 | 86.00 | 86.46 | 101.00 | 93.33
Norm | 93.68 | 86.31 | 98.59 | 95.61

## Slide 27: LRZ Energy Forecasts

## Slide 28: Retail Sales vs. Metered Load
The state-level forecasts are developed for retail sales (customer level) but the LRZ forecasts need to be for metered loads (substation level)
The difference is primarily due to losses on the distribution system
We have calculated an adjustment based on historical data (2011-2014)

## Slide 29: LRZ Gross* Metered Load (GWh)
* Without adjustment for EE programs
Year | LRZ1 | LRZ2 | LRZ3 | LRZ4 | LRZ5 | LRZ6 | LRZ7 | LRZ8 | LRZ9 | LRZ10
2015 | 96,613 | 64,572 | 47,074 | 49,243 | 41,938 | 98,266 | 99,885 | 36,631 | 111,306 | 22,294
2016 | 101,800 | 67,413 | 48,003 | 51,128 | 44,164 | 102,187 | 104,059 | 38,822 | 106,783 | 22,842
2017 | 103,657 | 69,032 | 48,626 | 51,601 | 44,801 | 103,760 | 105,499 | 39,889 | 110,054 | 23,363
2018 | 105,517 | 70,620 | 49,391 | 51,943 | 45,442 | 105,309 | 107,523 | 40,693 | 112,418 | 23,693
2019 | 107,422 | 71,847 | 50,326 | 52,409 | 46,013 | 106,920 | 109,076 | 41,189 | 113,442 | 24,110
2020 | 109,430 | 72,810 | 51,244 | 52,839 | 46,609 | 108,465 | 110,025 | 41,486 | 114,289 | 24,535
2021 | 111,359 | 73,670 | 52,036 | 53,122 | 47,142 | 109,966 | 110,503 | 41,740 | 114,689 | 24,990
2022 | 113,274 | 74,705 | 52,838 | 53,384 | 47,694 | 111,357 | 111,260 | 42,069 | 115,380 | 25,416
2023 | 115,080 | 75,782 | 53,682 | 53,655 | 48,296 | 112,701 | 112,040 | 42,488 | 116,447 | 25,806
2024 | 116,830 | 76,834 | 54,553 | 53,989 | 48,936 | 114,057 | 113,164 | 42,946 | 117,744 | 26,196
2025 | 118,635 | 77,799 | 55,458 | 54,297 | 49,549 | 115,408 | 114,214 | 43,419 | 118,627 | 26,604
2026 | 120,469 | 78,843 | 56,398 | 54,644 | 50,122 | 116,780 | 115,186 | 43,913 | 119,744 | 27,022
Compound Annual Growth Rates (%) |  |  |  |  |  |  |  |  |  | 
2017-2026 | 1.68 | 1.49 | 1.66 | 0.64 | 1.25 | 1.32 | 0.98 | 1.07 | 0.94 | 1.63

## Slide 30: EE/DR/DG Adjustment
Adjustment is done at the LRZ level using data provided by MISO from the MTEP process
AEG study was used and the amount selected by EGEAS in the Policy Regulations future is used here
  The adjustment this year is smaller than last year

## Slide 31: LRZ Net* Metered Load (GWh)
* With adjustment for EE energy impact at LRZ level
Year | LRZ1 | LRZ2 | LRZ3 | LRZ4 | LRZ5 | LRZ6 | LRZ7 | LRZ8 | LRZ9 | LRZ10
2015 | 96,613 | 64,572 | 47,074 | 49,243 | 41,938 | 98,266 | 99,885 | 36,631 | 111,306 | 22,294
2016 | 101,599 | 67,318 | 47,763 | 50,970 | 44,084 | 102,071 | 103,761 | 38,780 | 106,747 | 22,842
2017 | 103,376 | 68,933 | 48,204 | 51,350 | 44,650 | 103,581 | 105,089 | 39,843 | 109,988 | 23,363
2018 | 105,149 | 70,519 | 48,786 | 51,596 | 45,219 | 105,063 | 106,998 | 40,644 | 112,320 | 23,693
2019 | 106,961 | 71,742 | 49,536 | 51,964 | 45,717 | 106,602 | 108,432 | 41,136 | 113,306 | 24,110
2020 | 108,867 | 72,702 | 50,268 | 52,294 | 46,237 | 108,071 | 109,257 | 41,428 | 114,109 | 24,535
2021 | 110,682 | 73,560 | 50,871 | 52,474 | 46,693 | 109,491 | 109,606 | 41,678 | 114,460 | 24,990
2022 | 112,481 | 74,592 | 51,483 | 52,632 | 47,167 | 110,796 | 110,232 | 42,003 | 115,097 | 25,416
2023 | 114,163 | 75,666 | 52,133 | 52,797 | 47,690 | 112,050 | 110,874 | 42,417 | 116,104 | 25,806
2024 | 115,783 | 76,716 | 52,808 | 53,021 | 48,248 | 113,310 | 111,858 | 42,870 | 117,336 | 26,196
2025 | 117,449 | 77,677 | 53,513 | 53,218 | 48,778 | 114,559 | 112,762 | 43,338 | 118,148 | 26,604
2026 | 119,138 | 78,718 | 54,249 | 53,453 | 49,267 | 115,824 | 113,584 | 43,827 | 119,188 | 27,022
Compound Annual Growth Rates (%) |  |  |  |  |  |  |  |  |  | 
2017-2026 | 1.59 | 1.49 | 1.32 | 0.45 | 1.10 | 1.25 | 0.87 | 1.06 | 0.90 | 1.63

## Slide 32: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 96612.7802 | 101799.8281 | 103656.8499 | 105516.7175 | 107422.0802 | 109430.4003 | 111359.2096 | 113273.5846 | 115079.7421 | 116830.4564 | 118634.6325 | 120469.3768
2016 Net Energy | 96612.7802 | 101598.7182 | 103375.6051 | 105148.8782 | 106960.617 | 108866.7928 | 110682.1783 | 112480.5257 | 114163.3706 | 115783.1437 | 117449.1412 | 119137.7412
2015 Gross Energy | 99623.34 | 99937.5114 | 101565.1501 | 103429.0984 | 105122.7175 | 106833.7622 | 108715.8528 | 110538.9126 | 112350.5105 | 114082.5177 | 115768.9021 | 117445.2877
2015 Net Energy | 99623.34 | 99709.7087 | 101202.7036 | 102919.8221 | 104453.9527 | 105991.1231 | 107683.0211 | 109310.1794 | 110914.6433 | 112428.2363 | 113885.1322 | 115330.9969

## Slide 33: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 64571.9711 | 67412.9948 | 69031.7326 | 70620.4231 | 71846.8187 | 72809.5637 | 73669.6207 | 74705.1703 | 75781.7056 | 76834.2439 | 77799.088 | 78843.097
2016 Net Energy | 64571.9711 | 67317.7486 | 68932.9034 | 70518.7813 | 71742.3915 | 72702.3126 | 73559.5188 | 74592.1853 | 75665.877 | 76715.5166 | 77677.4371 | 78718.4561
2015 Gross Energy | 65112.694 | 67057.5045 | 68040.1964 | 69094.0357 | 70147.5762 | 71398.0644 | 72600.4432 | 73577.6214 | 74475.8237 | 75443.0204 | 76435.638 | 77426.2654
2015 Net Energy | 65112.694 | 66772.1275 | 67618.7915 | 68543.5522 | 69471.3349 | 70598.1609 | 71683.312 | 72553.8131 | 73350.6633 | 74220.9798 | 75120.0214 | 76056.8434

## Slide 34: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 47073.6553 | 48002.8665 | 48625.6125 | 49390.542 | 50325.5841 | 51244.2654 | 52036.2199 | 52838.1314 | 53682.0872 | 54553.487 | 55458.1232 | 56398.1828
2016 Net Energy | 47073.6553 | 47763.2277 | 48204.2135 | 48785.6133 | 49535.652 | 50267.6034 | 50871.1912 | 51482.8187 | 52133.2626 | 52808.1942 | 53512.9998 | 54248.9607
2015 Gross Energy | 47437.276 | 47431.7067 | 48085.563 | 48749.2963 | 49612.9679 | 50426.3115 | 51258.4269 | 52042.1947 | 52870.6625 | 53670.7475 | 54472.8112 | 55274.1202
2015 Net Energy | 47437.276 | 47140.1662 | 47557.8897 | 47981.9064 | 48602.4606 | 49168.9612 | 49751.5512 | 50282.8488 | 50854.5228 | 51393.918 | 51930.8017 | 52467.5607

## Slide 35: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 49243.14 | 51128.3711 | 51600.8552 | 51943.2862 | 52408.8679 | 52839.2487 | 53121.7603 | 53383.9117 | 53655.1445 | 53988.5733 | 54296.8018 | 54643.9967
2016 Net Energy | 49243.14 | 50970.4613 | 51349.7447 | 51596.4839 | 51964.0714 | 52294.1938 | 52474.3012 | 52631.9578 | 52796.5672 | 53021.2011 | 53218.4505 | 53452.5524
2015 Gross Energy | 50332.302 | 51069.1378 | 51501.0587 | 51819.8652 | 52122.6084 | 52564.6962 | 52989.4226 | 53313.9684 | 53602.329 | 53855.4514 | 54157.4645 | 54473.3198
2015 Net Energy | 50332.302 | 50777.3175 | 51016.9065 | 51142.8437 | 51252.8787 | 51501.3915 | 51733.5248 | 51865.7142 | 51962.2045 | 52023.994 | 52134.528 | 52279.8105

## Slide 36: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 41937.7013 | 44164.3754 | 44801.0077 | 45441.5228 | 46013.4567 | 46609.2922 | 47141.7514 | 47694.0303 | 48296.3282 | 48936.0569 | 49548.9858 | 50122.1531
2016 Net Energy | 41937.7013 | 44083.7072 | 44650.0442 | 45218.5025 | 45716.7413 | 46237.2853 | 46692.9659 | 47167.0547 | 47689.6756 | 48248.1823 | 48778.3506 | 49267.2587
2015 Gross Energy | 43298.145 | 44176.2537 | 44815.3123 | 45244.5012 | 45609.788 | 46044.3834 | 46604.202 | 47117.0607 | 47621.2473 | 48090.7856 | 48533.2292 | 48879.5058
2015 Net Energy | 43298.145 | 43920.166 | 44358.3238 | 44588.0984 | 44754.5623 | 44990.2717 | 45353.6101 | 45671.9446 | 45982.9778 | 46260.8051 | 46512.479 | 46694.3314

## Slide 37: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 98265.9011 | 102187.0851 | 103760.2155 | 105309.0084 | 106919.5869 | 108465.1152 | 109965.8047 | 111356.7235 | 112701.3628 | 114057.2371 | 115407.8742 | 116779.5958
2016 Net Energy | 98265.9011 | 102070.683 | 103581.21 | 105063.0701 | 106602.1651 | 108071.2776 | 109490.8945 | 110796.1529 | 112049.8455 | 113309.6308 | 114559.1376 | 115824.3005
2015 Gross Energy | 101810.806 | 102049.0144 | 103337.019 | 104481.1381 | 105764.0184 | 107269.647 | 108825.9568 | 110211.0016 | 111427.147 | 112642.7606 | 113870.1319 | 115113.704
2015 Net Energy | 101810.806 | 101723.8895 | 102781.9301 | 103689.5068 | 104728.7564 | 105982.7484 | 107282.4604 | 108405.3341 | 109352.9655 | 110293.7295 | 111238.536 | 112213.9189

## Slide 38: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 99885.4027 | 104058.7897 | 105498.7951 | 107522.8632 | 109076.122 | 110025.0617 | 110502.574 | 111260.2694 | 112039.5605 | 113163.8839 | 114213.7098 | 115185.7012
2016 Net Energy | 99885.4027 | 103760.899 | 105089.0109 | 106997.7357 | 108431.5369 | 109256.6516 | 109606.2194 | 110231.6836 | 110874.4314 | 111857.7301 | 112761.9414 | 113583.5227
2015 Gross Energy | 100152.488 | 102860.4105 | 103716.5423 | 105012.091 | 105594.8454 | 106389.9026 | 107890.0906 | 108893.5153 | 109337.762 | 110193.1109 | 111199.701 | 112274.1607
2015 Net Energy | 100152.488 | 102386.6148 | 103005.2989 | 104060.331 | 104398.0557 | 104942.5472 | 106190.1511 | 106938.2726 | 107124.2375 | 107718.5408 | 108460.2061 | 109295.1445

## Slide 39: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 36631.4496 | 38822.4691 | 39888.9717 | 40693.301 | 41189.3829 | 41486.1585 | 41739.6684 | 42068.9855 | 42487.9921 | 42945.9789 | 43419.1167 | 43912.7269
2016 Net Energy | 36631.4496 | 38780.4916 | 39843.1015 | 40643.5697 | 41135.6521 | 41428.3495 | 41677.6102 | 42002.5176 | 42416.9476 | 42870.1878 | 43338.4098 | 43826.9384
2015 Gross Energy | 37159.745 | 37949.168 | 38275.2246 | 38649.5418 | 39076.125 | 39703.8941 | 40209.4355 | 40519.672 | 40805.3961 | 41119.9295 | 41500.5884 | 41861.5747
2015 Net Energy | 37159.745 | 37857.3103 | 38128.3274 | 38445.712 | 38813.0751 | 39379.6097 | 39821.5362 | 40065.9612 | 40283.609 | 40527.7449 | 40835.6522 | 41122.9397

## Slide 40: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 111306.2244 | 106782.9733 | 110053.8855 | 112418.3442 | 113441.7721 | 114288.5604 | 114688.8336 | 115380.354 | 116447.3642 | 117743.6717 | 118627.0402 | 119744.4004
2016 Net Energy | 111306.2244 | 106746.828 | 109988.2968 | 112320.4749 | 113305.885 | 114108.8751 | 114459.5382 | 115097.0589 | 116104.498 | 117335.5222 | 118147.7085 | 119188.0474
2015 Gross Energy | 110904.567 | 111533.8265 | 113524.8518 | 115434.2688 | 117631.3591 | 120329.544 | 122925.6063 | 125123.3102 | 127209.4485 | 129470.2834 | 131833.9563 | 134300.6926
2015 Net Energy | 110904.567 | 111480.8546 | 113418.5467 | 115266.4235 | 117390.8645 | 120005.3857 | 122507.3979 | 124602.0569 | 126575.1997 | 128713.1452 | 130943.702 | 133271.2821

## Slide 41: LRZ Energy Forecast
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 22293.7285 | 22841.9337 | 23362.6 | 23692.6717 | 24110.221 | 24534.9599 | 24989.6012 | 25416.1914 | 25805.9816 | 26196.3959 | 26604.4224 | 27022.0695
2016 Net Energy | 22293.7285 | 22841.9337 | 23362.6 | 23692.6717 | 24110.221 | 24534.9599 | 24989.6012 | 25416.1914 | 25805.9816 | 26196.3959 | 26604.4224 | 27022.0695
2015 Gross Energy | 21998.662 | 22917.3562 | 23328.5615 | 23725.9448 | 24250.4245 | 24757.7917 | 25223.7653 | 25628.1241 | 26028.055 | 26445.1228 | 26866.5798 | 27292.8496
2015 Net Energy | 21998.662 | 22894.3109 | 23287.073 | 23665.4348 | 24170.165 | 24656.9938 | 25102.1067 | 25485.2074 | 25863.4471 | 26258.4364 | 26657.2843 | 27064.6758

## Slide 42: LRZ Peak Demand

## Slide 43: Metered Load vs. Resource Needs
The peak demand forecasts are developed for metered loads (substation level) but resource needs are determined at the generator level
The difference is primarily due to losses on the transmission system
We have NOT calculated an adjustment because we do not have the necessary data

## Slide 44: LRZ Non-coincident Peaks
The following slides provide LRZ summer and winter peak demands that are non-coincident with the MISO peak
Thus, the arithmetic sum of the LRZ peaks is greater than the MISO coincident peak

## Slide 45: Gross Summer Non-coincident Peak (Metered Load in MW)
Year | LRZ1 | LRZ2 | LRZ3 | LRZ4 | LRZ5 | LRZ6 | LRZ7 | LRZ8 | LRZ9 | LRZ10
2015 | 16,935 | 11,604 | 8,751 | 9,280 | 8,361 | 17,297 | 19,994 | 7,486 | 21,071 | 4,755
2016 | 18,214 | 12,617 | 8,983 | 9,794 | 8,789 | 17,810 | 21,164 | 7,778 | 19,232 | 4,765
2017 | 18,546 | 12,920 | 9,100 | 9,884 | 8,916 | 18,084 | 21,457 | 7,991 | 19,821 | 4,874
2018 | 18,879 | 13,217 | 9,243 | 9,950 | 9,043 | 18,354 | 21,868 | 8,152 | 20,247 | 4,943
2019 | 19,220 | 13,447 | 9,418 | 10,039 | 9,157 | 18,635 | 22,184 | 8,252 | 20,431 | 5,030
2020 | 19,579 | 13,627 | 9,590 | 10,122 | 9,275 | 18,904 | 22,377 | 8,311 | 20,583 | 5,118
2021 | 19,924 | 13,788 | 9,738 | 10,176 | 9,381 | 19,166 | 22,474 | 8,362 | 20,656 | 5,213
2022 | 20,267 | 13,982 | 9,888 | 10,226 | 9,491 | 19,408 | 22,629 | 8,428 | 20,780 | 5,302
2023 | 20,590 | 14,183 | 10,046 | 10,278 | 9,611 | 19,643 | 22,787 | 8,512 | 20,972 | 5,383
2024 | 20,903 | 14,380 | 10,209 | 10,342 | 9,739 | 19,879 | 23,016 | 8,604 | 21,206 | 5,465
2025 | 21,226 | 14,561 | 10,378 | 10,401 | 9,860 | 20,115 | 23,229 | 8,699 | 21,365 | 5,550
2026 | 21,554 | 14,756 | 10,554 | 10,467 | 9,975 | 20,354 | 23,427 | 8,797 | 21,566 | 5,637
Compound Annual Growth Rates (%) |  |  |  |  |  |  |  |  |  | 
2017-2026 | 1.68 | 1.49 | 1.66 | 0.64 | 1.25 | 1.32 | 0.98 | 1.07 | 0.94 | 1.63

## Slide 46: Net Summer Non-coincident Peak with EE Adjustment (Metered Load in MW)
Year | LRZ1 | LRZ2 | LRZ3 | LRZ4 | LRZ5 | LRZ6 | LRZ7 | LRZ8 | LRZ9 | LRZ10
2015 | 16,935 | 11,604 | 8,751 | 9,280 | 8,361 | 17,297 | 19,994 | 7,486 | 21,071 | 4,755
2016 | 16,807 | 11,399 | 8,444 | 9,622 | 8,775 | 17,332 | 19,800 | 7,291 | 18,986 | 4,765
2017 | 17,062 | 11,656 | 8,507 | 9,693 | 8,890 | 17,581 | 20,047 | 7,488 | 19,548 | 4,874
2018 | 17,322 | 11,918 | 8,594 | 9,739 | 9,006 | 17,825 | 20,413 | 7,635 | 19,951 | 4,943
2019 | 17,589 | 12,112 | 8,713 | 9,807 | 9,107 | 18,079 | 20,681 | 7,721 | 20,111 | 5,030
2020 | 17,869 | 12,256 | 8,829 | 9,869 | 9,213 | 18,320 | 20,824 | 7,767 | 20,237 | 5,118
2021 | 18,125 | 12,380 | 8,920 | 9,902 | 9,306 | 18,552 | 20,871 | 7,804 | 20,279 | 5,213
2022 | 18,390 | 12,537 | 9,014 | 9,931 | 9,403 | 18,764 | 20,973 | 7,857 | 20,382 | 5,302
2023 | 18,635 | 12,702 | 9,114 | 9,961 | 9,510 | 18,967 | 21,079 | 7,927 | 20,552 | 5,383
2024 | 18,868 | 12,862 | 9,218 | 10,002 | 9,623 | 19,171 | 21,254 | 8,004 | 20,762 | 5,465
2025 | 19,110 | 13,005 | 9,329 | 10,039 | 9,732 | 19,373 | 21,413 | 8,085 | 20,896 | 5,550
2026 | 19,355 | 13,162 | 9,444 | 10,082 | 9,832 | 19,578 | 21,556 | 8,169 | 21,070 | 5,637
Compound Annual Growth Rates (%) |  |  |  |  |  |  |  |  |  | 
2017-2026 | 1.41 | 1.36 | 1.17 | 0.44 | 1.12 | 1.20 | 0.81 | 0.97 | 0.84 | 1.63

## Slide 47: Gross Winter Non-coincident Peak (Metered Load in MW)
Year | LRZ1 | LRZ2 | LRZ3 | LRZ4 | LRZ5 | LRZ6 | LRZ7 | LRZ8 | LRZ9 | LRZ10
2015 | 15,109 | 9,773 | 7,274 | 8,168 | 7,431 | 16,768 | 14,958 | 6,880 | 18,698 | 4,200
2016 | 15,212 | 9,950 | 7,260 | 7,909 | 7,392 | 16,079 | 15,109 | 6,477 | 17,099 | 4,090
2017 | 15,489 | 10,189 | 7,354 | 7,982 | 7,498 | 16,327 | 15,318 | 6,655 | 17,623 | 4,184
2018 | 15,767 | 10,424 | 7,470 | 8,035 | 7,605 | 16,570 | 15,612 | 6,789 | 18,001 | 4,243
2019 | 16,052 | 10,605 | 7,611 | 8,107 | 7,701 | 16,824 | 15,838 | 6,872 | 18,165 | 4,317
2020 | 16,352 | 10,747 | 7,750 | 8,174 | 7,801 | 17,067 | 15,975 | 6,921 | 18,301 | 4,393
2021 | 16,640 | 10,874 | 7,870 | 8,218 | 7,890 | 17,303 | 16,045 | 6,964 | 18,365 | 4,475
2022 | 16,926 | 11,027 | 7,991 | 8,258 | 7,982 | 17,522 | 16,155 | 7,018 | 18,476 | 4,551
2023 | 17,196 | 11,186 | 8,119 | 8,300 | 8,083 | 17,733 | 16,268 | 7,088 | 18,646 | 4,621
2024 | 17,457 | 11,341 | 8,251 | 8,352 | 8,190 | 17,947 | 16,431 | 7,165 | 18,854 | 4,691
2025 | 17,727 | 11,483 | 8,387 | 8,399 | 8,293 | 18,159 | 16,583 | 7,244 | 18,996 | 4,764
2026 | 18,001 | 11,637 | 8,529 | 8,453 | 8,389 | 18,375 | 16,725 | 7,326 | 19,174 | 4,839
Compound Annual Growth Rates (%) |  |  |  |  |  |  |  |  |  | 
2017-2026 | 1.68 | 1.49 | 1.66 | 0.64 | 1.25 | 1.32 | 0.98 | 1.07 | 0.94 | 1.63

## Slide 48: Net Winter Non-coincident Peak with EE Adjustment (Metered Load in MW)
Year | LRZ1 | LRZ2 | LRZ3 | LRZ4 | LRZ5 | LRZ6 | LRZ7 | LRZ8 | LRZ9 | LRZ10
2015 | 15,109 | 9,773 | 7,274 | 8,168 | 7,431 | 16,768 | 14,958 | 6,880 | 18,698 | 4,200
2016 | 13,805 | 8,733 | 6,721 | 7,737 | 7,378 | 15,601 | 13,745 | 5,990 | 16,854 | 4,090
2017 | 14,005 | 8,926 | 6,761 | 7,791 | 7,473 | 15,823 | 13,908 | 6,152 | 17,350 | 4,184
2018 | 14,210 | 9,124 | 6,821 | 7,824 | 7,568 | 16,041 | 14,156 | 6,272 | 17,706 | 4,243
2019 | 14,421 | 9,270 | 6,906 | 7,875 | 7,652 | 16,267 | 14,334 | 6,340 | 17,846 | 4,317
2020 | 14,642 | 9,376 | 6,989 | 7,921 | 7,739 | 16,482 | 14,422 | 6,377 | 17,954 | 4,393
2021 | 14,841 | 9,466 | 7,052 | 7,944 | 7,815 | 16,689 | 14,441 | 6,406 | 17,988 | 4,475
2022 | 15,049 | 9,582 | 7,117 | 7,963 | 7,894 | 16,878 | 14,499 | 6,447 | 18,078 | 4,551
2023 | 15,241 | 9,704 | 7,186 | 7,983 | 7,982 | 17,058 | 14,560 | 6,503 | 18,226 | 4,621
2024 | 15,422 | 9,822 | 7,260 | 8,012 | 8,075 | 17,239 | 14,670 | 6,565 | 18,410 | 4,691
2025 | 15,611 | 9,927 | 7,337 | 8,037 | 8,164 | 17,418 | 14,768 | 6,630 | 18,526 | 4,764
2026 | 15,802 | 10,043 | 7,419 | 8,068 | 8,246 | 17,600 | 14,853 | 6,698 | 18,679 | 4,839
Compound Annual Growth Rates (%) |  |  |  |  |  |  |  |  |  | 
2017-2026 | 1.35 | 1.32 | 1.04 | 0.39 | 1.10 | 1.19 | 0.73 | 0.95 | 0.82 | 1.63

## Slide 49: LRZ 1 Non-coincident Peak (MW)
Chart: LRZ1
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 16935.2784 | 18213.8535 | 18546.1087 | 18878.8731 | 19219.7774 | 19579.1026 | 19924.2019 | 20266.7186 | 20589.8733 | 20903.1081 | 21225.9083 | 21554.1776
Summer NCP with EE/DR/DG adjustment | 16935.2784 | 16807.1344 | 17062.175 | 17321.7143 | 17588.895 | 17869.4565 | 18125.0585 | 18390.1735 | 18634.7277 | 18867.8264 | 19109.7348 | 19355.2953
Winter NCP without EE/DR/DG adjustment | 15109.0448 | 15211.5097 | 15488.9965 | 15766.9085 | 16051.6186 | 16351.7132 | 16639.9269 | 16925.9837 | 17195.87 | 17457.4717 | 17727.062 | 18001.2199
Winter NCP with EE/DR/DG adjustment | 15109.0448 | 13804.7906 | 14005.0628 | 14209.7497 | 14420.7362 | 14642.0671 | 14840.7835 | 15049.4386 | 15240.7244 | 15422.19 | 15610.8885 | 15802.3376

## Slide 50: LRZ 2 Non-coincident Peak (MW)
Chart: LRZ2
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 11603.8468 | 12616.8924 | 12919.8524 | 13217.1888 | 13446.7187 | 13626.9043 | 13787.871 | 13981.6826 | 14183.165 | 14380.1561 | 14560.7345 | 14756.1293
Summer NCP with EE/DR/DG adjustment | 11603.8468 | 11399.2323 | 11656.1648 | 11917.5824 | 12111.5164 | 12255.6135 | 12380.0946 | 12536.9488 | 12701.9521 | 12861.75 | 13004.7846 | 13161.7569
Winter NCP without EE/DR/DG adjustment | 9773.1305 | 9950.281 | 10189.2097 | 10423.7033 | 10604.7215 | 10746.8244 | 10873.7704 | 11026.6194 | 11185.518 | 11340.8746 | 11483.2873 | 11637.385
Winter NCP with EE/DR/DG adjustment | 9773.1305 | 8732.6209 | 8925.5221 | 9124.0969 | 9269.5192 | 9375.5336 | 9465.994 | 9581.8856 | 9704.3051 | 9822.4685 | 9927.3374 | 10043.0126

## Slide 51: LRZ 3 Non-coincident Peak (MW)
Chart: LRZ3
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 8751.405 | 8983.2447 | 9099.7853 | 9242.934 | 9417.9175 | 9589.8393 | 9738.0455 | 9888.115 | 10046.0527 | 10209.1263 | 10378.4196 | 10554.3422
Summer NCP with EE/DR/DG adjustment | 8751.405 | 8444.0822 | 8506.8214 | 8594.1458 | 8713.0834 | 8828.7126 | 8920.4247 | 9013.6808 | 9113.7447 | 9218.3874 | 9328.5291 | 9444.1877
Winter NCP without EE/DR/DG adjustment | 7273.9289 | 7259.8128 | 7353.9951 | 7469.6807 | 7611.0938 | 7750.0324 | 7869.8053 | 7991.0841 | 8118.7215 | 8250.5094 | 8387.3239 | 8529.4958
Winter NCP with EE/DR/DG adjustment | 7273.9289 | 6720.6503 | 6761.0312 | 6820.8925 | 6906.2597 | 6988.9057 | 7052.1845 | 7116.6499 | 7186.4135 | 7259.7705 | 7337.4334 | 7419.3413

## Slide 52: LRZ 4 Non-coincident Peak (MW)
Chart: LRZ4
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 9280.3934 | 9793.8921 | 9884.3987 | 9949.9931 | 10039.1776 | 10121.6191 | 10175.7356 | 10225.952 | 10277.908 | 10341.7779 | 10400.8206 | 10467.3275
Summer NCP with EE/DR/DG adjustment | 9280.3934 | 9622.0771 | 9693.0527 | 9738.5822 | 9807.3401 | 9868.9863 | 9901.9473 | 9930.6528 | 9960.7276 | 10002.338 | 10038.7303 | 10082.2217
Winter NCP without EE/DR/DG adjustment | 8167.6907 | 7909.1701 | 7982.2597 | 8035.2312 | 8107.2532 | 8173.8298 | 8217.5322 | 8258.085 | 8300.0427 | 8351.6216 | 8399.3022 | 8453.0106
Winter NCP with EE/DR/DG adjustment | 8167.6907 | 7737.3551 | 7790.9137 | 7823.8203 | 7875.4157 | 7921.197 | 7943.7439 | 7962.7858 | 7982.8623 | 8012.1817 | 8037.2119 | 8067.9048

## Slide 53: LRZ 5 Non-coincident Peak (MW)
Chart: LRZ5
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 8361.2047 | 8788.9325 | 8915.6256 | 9043.0913 | 9156.909 | 9275.4833 | 9381.4453 | 9491.3516 | 9611.2119 | 9738.5211 | 9860.497 | 9974.5602
Summer NCP with EE/DR/DG adjustment | 8361.2047 | 8775.4862 | 8890.4455 | 9005.8737 | 9107.3716 | 9213.3514 | 9306.4625 | 9403.2753 | 9509.7865 | 9623.4817 | 9731.58 | 9831.5089
Winter NCP without EE/DR/DG adjustment | 7431.3695 | 7391.6099 | 7498.1604 | 7605.3608 | 7701.083 | 7800.8056 | 7889.9211 | 7982.3537 | 8083.1579 | 8190.2266 | 8292.81 | 8388.7386
Winter NCP with EE/DR/DG adjustment | 7431.3695 | 7378.1636 | 7472.9803 | 7568.1432 | 7651.5456 | 7738.6737 | 7814.9383 | 7894.2774 | 7981.7325 | 8075.1872 | 8163.893 | 8245.6873

## Slide 54: LRZ 6 Non-coincident Peak (MW)
Chart: LRZ6
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 17297.2844 | 17810.2697 | 18084.4519 | 18354.3923 | 18635.1013 | 18904.4727 | 19166.0291 | 19408.4534 | 19642.8117 | 19879.1281 | 20114.5318 | 20353.6102
Summer NCP with EE/DR/DG adjustment | 17297.2844 | 17332.3897 | 17580.7865 | 17824.7588 | 18078.5564 | 18319.6118 | 18551.9846 | 18764.4885 | 18967.495 | 19171.3964 | 19373.4884 | 19578.0751
Winter NCP without EE/DR/DG adjustment | 16768.2895 | 16079.0533 | 16326.584 | 16570.2853 | 16823.7085 | 17066.8961 | 17303.0284 | 17521.8883 | 17733.4662 | 17946.8119 | 18159.3335 | 18375.1728
Winter NCP with EE/DR/DG adjustment | 16768.2895 | 15601.1733 | 15822.9186 | 16040.6518 | 16267.1636 | 16482.0352 | 16688.9839 | 16877.9234 | 17058.1495 | 17239.0802 | 17418.2901 | 17599.6377

## Slide 55: LRZ 7 Non-coincident Peak (MW)
Chart: LRZ7
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 19993.983 | 21163.8706 | 21456.7443 | 21868.407 | 22184.3146 | 22377.3136 | 22474.4318 | 22628.5348 | 22787.0299 | 23015.6991 | 23229.2167 | 23426.904
Summer NCP with EE/DR/DG adjustment | 19993.983 | 19800.3001 | 20047.0002 | 20412.5136 | 20680.5408 | 20824.0369 | 20870.6008 | 20973.002 | 21078.9182 | 21254.1609 | 21413.3066 | 21555.5632
Winter NCP without EE/DR/DG adjustment | 14957.5503 | 15109.0132 | 15318.0975 | 15611.9859 | 15837.5143 | 15975.2974 | 16044.6307 | 16154.6457 | 16267.7963 | 16431.0446 | 16583.4761 | 16724.6062
Winter NCP with EE/DR/DG adjustment | 14957.5503 | 13745.4427 | 13908.3534 | 14156.0925 | 14333.7405 | 14422.0207 | 14440.7997 | 14499.1129 | 14559.6846 | 14669.5064 | 14767.566 | 14853.2654

## Slide 56: LRZ 8 Non-coincident Peak (MW)
Chart: LRZ8
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 7486.0647 | 7777.6605 | 7991.3227 | 8152.4613 | 8251.846 | 8311.3017 | 8362.0897 | 8428.0648 | 8512.0082 | 8603.7609 | 8698.5489 | 8797.4384
Summer NCP with EE/DR/DG adjustment | 7486.0647 | 7291.0948 | 7488.0977 | 7635.0663 | 7720.5012 | 7766.8832 | 7804.3092 | 7856.6252 | 7926.6308 | 8004.1761 | 8084.5729 | 8168.9156
Winter NCP without EE/DR/DG adjustment | 6879.6803 | 6476.856 | 6654.7835 | 6788.9719 | 6871.7345 | 6921.2464 | 6963.5401 | 7018.481 | 7088.385 | 7164.7921 | 7243.727 | 7326.0773
Winter NCP with EE/DR/DG adjustment | 6879.6803 | 5990.2903 | 6151.5585 | 6271.5769 | 6340.3897 | 6376.8279 | 6405.7596 | 6447.0414 | 6503.0076 | 6565.2073 | 6629.751 | 6697.5545

## Slide 57: LRZ 9 Non-coincident Peak (MW)
Chart: LRZ9
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 21071.2586 | 19231.7259 | 19820.8206 | 20246.6621 | 20430.9826 | 20583.49 | 20655.5796 | 20780.1232 | 20972.2929 | 21205.7592 | 21364.8548 | 21566.0925
Summer NCP with EE/DR/DG adjustment | 21071.2586 | 18986.3786 | 19547.697 | 19951.463 | 20111.2883 | 20236.7444 | 20278.9169 | 20382.3757 | 20552.152 | 20761.8415 | 20895.7578 | 21070.4635
Winter NCP without EE/DR/DG adjustment | 18698.1491 | 17098.9439 | 17622.7086 | 18001.3246 | 18165.2041 | 18300.7986 | 18364.8935 | 18475.6253 | 18646.4835 | 18854.0586 | 18995.5107 | 19174.4313
Winter NCP with EE/DR/DG adjustment | 18698.1491 | 16853.5966 | 17349.585 | 17706.1255 | 17845.5098 | 17954.053 | 17988.2308 | 18077.8778 | 18226.3426 | 18410.1409 | 18526.4137 | 18678.8023

## Slide 58: LRZ 10 Non-coincident Peak (MW)
Chart: LRZ10
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer NCP without EE/DR/DG adjustment | 4754.79 | 4765.0427 | 4873.6586 | 4942.5147 | 5029.6194 | 5118.2239 | 5213.0664 | 5302.0572 | 5383.3711 | 5464.8152 | 5549.9333 | 5637.0585
Summer NCP with EE/DR/DG adjustment | 4754.79 | 4765.0427 | 4873.6586 | 4942.5147 | 5029.6194 | 5118.2239 | 5213.0664 | 5302.0572 | 5383.3711 | 5464.8152 | 5549.9333 | 5637.0585
Winter NCP without EE/DR/DG adjustment | 4200.3828 | 4090.3021 | 4183.5377 | 4242.6436 | 4317.4141 | 4393.4721 | 4474.8846 | 4551.2741 | 4621.0738 | 4690.9852 | 4764.0505 | 4838.8385
Winter NCP with EE/DR/DG adjustment | 4200.3828 | 4090.3021 | 4183.5377 | 4242.6436 | 4317.4141 | 4393.4721 | 4474.8846 | 4551.2741 | 4621.0738 | 4690.9852 | 4764.0505 | 4838.8385

## Slide 59: MISO Level Forecasts

## Slide 60: Energy and Peak Demand
The MISO system energy and peak demand projections here are at the metered load (substation) level
Energy is the arithmetic sum of the LRZ energy forecasts
Peak demand is determined using coincidence factors

## Slide 61: MISO Energy (Metered Load in GWh)
Year | MISO energy | MISO energy
 | without EE/DR/DG adjustment | with EE/DR/DG adjustment
2015 | 667,822 | 667,822
2016 | 687,202 | 685,935
2017 | 700,281 | 698,377
2018 | 712,549 | 709,986
2019 | 722,754 | 719,505
2020 | 731,733 | 727,768
2021 | 739,215 | 734,504
2022 | 747,377 | 741,898
2023 | 755,977 | 749,700
2024 | 765,250 | 758,146
2025 | 774,010 | 766,048
2026 | 783,121 | 774,270
Compound Annual Growth Rates (%) |  | 
2017-2026 | 1.25 | 1.15

## Slide 62: MISO Energy (Metered Load in GWh)
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016 Gross Energy | 667821.9543 | 687201.6867 | 700280.5257 | 712548.6799 | 722753.8925 | 731732.6259 | 739215.0439 | 747377.352 | 755977.2687 | 765249.985 | 774009.7947 | 783121.3001
2016 Net Energy | 667821.9543 | 685934.6983 | 698376.7301 | 709985.7814 | 719504.9334 | 727768.3016 | 734504.0188 | 741898.1466 | 749700.457 | 758145.7049 | 766047.9989 | 774269.8475
2015 Gross Energy | 677830.025 | 686981.8898 | 696189.4797 | 705639.7814 | 714932.4304 | 725717.9971 | 737243.202 | 746965.3809 | 755728.3817 | 765013.7298 | 774639.0025 | 784341.4806
2015 Net Energy | 677830.025 | 684662.466 | 692375.7912 | 700303.6309 | 708036.1059 | 717217.1932 | 727108.6714 | 735181.3322 | 742264.4705 | 749839.5301 | 757718.343 | 765797.5037

## Slide 63: Summer Coincidence Factors
LRZ | Average | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
1 | 0.946 | 0.968 | 1.000 | 0.945 | 0.973 | 0.896 | 0.891
2 | 0.978 | 0.948 | 1.000 | 0.969 | 0.999 | 1.000 | 0.950
3 | 0.953 | 0.952 | 0.986 | 0.974 | 0.969 | 0.992 | 0.848
4 | 0.964 | 1.000 | 0.988 | 0.945 | 0.988 | 0.885 | 0.976
5 | 0.965 | 1.000 | 0.971 | 0.949 | 0.963 | 0.907 | 0.999
6 | 0.983 | 0.968 | 0.991 | 0.973 | 1.000 | 0.970 | 0.995
7 | 0.979 | 0.913 | 0.961 | 1.000 | 0.999 | 0.998 | 1.000
8 | 0.932 | 0.964 | 0.936 | 0.929 | 0.936 | 0.875 | 0.950
9 | 0.921 | 0.982 | 0.917 | 0.912 | 0.860 | 0.920 | 0.937
10 | 0.893 | 0.960 | 0.901 | 0.894 | 0.791 | 0.844 | 0.968

## Slide 64: Winter Coincidence Factors
LRZ | Average | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
1 | 0.984 | 0.990 | 0.994 | 0.962 | 1.000 | 0.994 | 0.962
2 | 0.976 | 0.993 | 0.976 | 0.963 | 0.990 | 0.989 | 0.944
3 | 0.986 | 0.996 | 0.971 | 1.000 | 0.979 | 1.000 | 0.970
4 | 0.988 | 1.000 | 1.000 | 1.000 | 0.980 | 0.992 | 0.957
5 | 0.988 | 0.962 | 1.000 | 1.000 | 0.964 | 1.000 | 1.000
6 | 0.979 | 0.983 | 0.993 | 0.992 | 0.928 | 0.988 | 0.988
7 | 0.954 | 0.988 | 0.958 | 0.938 | 0.959 | 0.944 | 0.936
8 | 0.958 | 0.889 | 0.929 | 0.995 | 0.954 | 0.981 | 1.000
9 | 0.921 | 0.832 | 0.950 | 0.895 | 0.887 | 0.977 | 0.984
10 | 0.935 | 0.924 | 0.892 | 0.936 | 0.858 | 0.998 | 0.999

## Slide 65: Comparison to Last Year
2016 Study
LRZ | Summer | Winter
1 | 0.956 | 0.989
2 | 0.983 | 0.982
3 | 0.975 | 0.989
4 | 0.961 | 0.994
5 | 0.958 | 0.985
6 | 0.979 | 0.975
7 | 0.974 | 0.957
8 | 0.928 | 0.949
9 | 0.917 | 0.910
10 | 0.876 | 0.918
2015 Study
LRZ | Summer | Winter
1 | 0.946 | 0.984
2 | 0.978 | 0.976
3 | 0.953 | 0.986
4 | 0.964 | 0.988
5 | 0.965 | 0.988
6 | 0.983 | 0.979
7 | 0.979 | 0.954
8 | 0.932 | 0.958
9 | 0.921 | 0.921
10 | 0.893 | 0.935

## Slide 66: MISO Coincident Peak Demand (Metered Load in MW)
Year | MISO Summer CP without | MISO Summer CP with | MISO Winter CP without | MISO Winter CP with
 | EE/DR/DG adjustment | EE/DR/DG adjustment | EE/DR/DG adjustment | EE/DR/DG adjustment
2015 | 119,609 | 119,609 | 106,100 | 106,100
2016 | 123,475 | 117,553 | 102,864 | 96,942
2017 | 125,801 | 119,554 | 104,822 | 98,575
2018 | 128,001 | 121,449 | 106,648 | 100,095
2019 | 129,836 | 122,972 | 108,173 | 101,309
2020 | 131,438 | 124,252 | 109,521 | 102,335
2021 | 132,768 | 125,243 | 110,650 | 103,125
2022 | 134,224 | 126,376 | 111,877 | 104,029
2023 | 135,756 | 127,580 | 113,169 | 104,992
2024 | 137,414 | 128,902 | 114,558 | 106,047
2025 | 138,983 | 130,130 | 115,873 | 107,020
2026 | 140,610 | 131,407 | 117,241 | 108,038
Compound Annual Growth Rates (%) |  |  |  | 
2017-2026 | 1.24 | 1.06 | 1.25 | 1.02

## Slide 67: 90/10 Net Forecasts: CAGR 2017-2026
 | BASE | HIGH | LOW
Energy | 1.15 | 1.58 | 0.65
Summer Peak | 1.06 | 1.51 | 0.52
Winter Peak | 1.02 | 1.48 | 0.49

## Slide 68: MISO Coincident Peak Demand (Metered Load in MW)
Chart: MISO System
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Summer CP without EE/DR/DG adjustment | 119608.5916 | 123475.4154 | 125801.1902 | 128001.3019 | 129835.8888 | 131438.2357 | 132768.168 | 134223.7992 | 135755.957 | 137413.9376 | 138982.9223 | 140610.0004
Summer CP with EE/DR/DG adjustment | 119608.5916 | 117553.2489 | 119554.3208 | 121448.999 | 122972.2373 | 124252.1057 | 125242.5376 | 126376.0258 | 127579.738 | 128902.2592 | 130129.8746 | 131407.4064
Winter CP without EE/DR/DG adjustment | 106099.8361 | 102864.0953 | 104822.0399 | 106647.7318 | 108172.7486 | 109520.6615 | 110650.1824 | 111876.7687 | 113168.6796 | 114558.4257 | 115873.4344 | 117240.8554
Winter CP with EE/DR/DG adjustment | 106099.8361 | 96941.9288 | 98575.1705 | 100095.4289 | 101309.0971 | 102334.5315 | 103124.552 | 104028.9953 | 104992.4606 | 106046.7473 | 107020.3867 | 108038.2614

## Slide 69: Next Steps
Present to the October/November PAC meetings
Continue work on attempting to quantify embedded DSM
Report is due November 1, including low/high forecasts
Comments and suggestions would be greatly appreciated

## Slide 70: Contact Information
State Utility Forecasting Group
765-494-4223
http://www.purdue.edu/discoverypark/energy/SUFG/
Doug Gotham
765-494-0851
gotham@purdue.edu